## Feeder 9A Bid Form
VIRGIN ISLANDS WATER & POWER AUTHORITY
CHARLOTTE AMALIE - UNDERGROUND ELECTRIC CONSTRUCTION PROJECT
FEEDER 9A, Phase 1, Construction Bid Form, 05-21-25
ST. THOMAS U.S. VIRGIN ISLANDS
Item | Quantity | Unit | Description | Unit Cost | Total Cost
GENERAL
1A | 1 | Lot | Mobilization
1B | 1 | Lot | Bonding: Bid Guarantee, Performance Bond, Payment Bond
2 | 1 | Lot | Construction Impact Mitigation including Stormwater / Sediment & Erosion Control, Dust Control, Dewatering, Noise Control, Vibration Control, Landscaping & Brush / Tree Removal & Protection
3A | 1 | Lot | Traffic Control/Traffic Control Devices/Road Closure Permits
3B | 1 | Lot | Traffic Control/Traffic Control Devices/Road Closure Permits (cable only areas)
4A | 1 | Lot | Specialty Consulting Services: Archaologist
4B | 1 | Lot | Specialty Consulting Services: Arborist
4C | 1 | Lot | Specialty Consulting Services:SUE Engineer/ Surveyor/Civil Engineer
4D | 1 | Lot | Special Inspection Services (soils, concrete, anchors)
4E | 1 | Lot | Asphalt testing Agency
5 | 1 | Lot | Project Cleanup, Punchlist, Demobilization, Closeout
6 | 1 | Lot | General Demolition: Remove & dispose of existing items as required to clear areas for new construction, in accordance with contract documents (including, but not limited to transclosure, bollards, concrete pads, rubbish & debris, etc.)
Subtotal General
CIVIL WORK
7 |  |  | Duct Banks: Including roadway/driveway cutting, excavation, PVC conduits, spacers, elbows, couplings, pull lines, warning tape, concrete envelope (where required per section details), Control Density Fill, roadway patching
7-A | 2373 | Linear Feet | Duct Bank Section A-A: 3-4” PVC in CDF (Refer to Drawing 104 for Duct Bank Details)
7-B | 671 | Linear Feet | Duct Bank Section B-B: 4-4” PVC in CDF (Refer to Drawing E-104 for Duct Bank Details)
7-C | 925 | Linear Feet | Duct Bank Section C-C: 2-4” PVC in CDF (Refer to Drawing E-104 for Duct Bank Details
7-D | 477 | Linear Feet | Duct Bank Section D-D: 5-4” PVC in CDF- Refer to E-104 for Duct Bank Details
7-E | 183 | Linear Feet | Duct Bank Section E-E: 6-4" PVC in CDF (Refer to Drawing E-104 for Duct Bank Details)
7-F | 0 | Linear Feet | Duct Bank Section F-F: 3-4”, 1-2" PVC in CDF (Refer to Drawing 104 for Duct Bank Details)
7-J | 591 | Linear Feet | Duct Bank Section J-J: 1-2" PVC (DIRECT BURIAL) (Refer to Drawing E-104 for Duct Bank Details)
7-K | 31 | Linear Feet | Duct Bank Section K-K: 4-4", 1-2" PVC in CDF (Refer to Drawing E-104 for Duct Bank Details)
7-L | 887 | Linear Feet | Duct Bank Section L-L: 1-4" PVC in CDF (Refer to Drawing E-104 for Duct Bank Details)
7-M | 220 | Linear Feet | Duct Bank Section M-M: 2-6”,1-4" PVC in Concrete/CDF (Refer to Drawing E-104 for Duct Bank Details)
7-O | 34 | Linear Feet | Duct Bank Section O-O: 4-6”,3-4",2-2" PVC in Concrete/CDF (Refer to Drawing E-104 for Duct Bank Details)
7-P | 24 | Linear Feet | Duct Bank Section P-P: 1-4",2-2" PVC in CDF (Refer to Drawing E-104 for Duct Bank Details)
7-Q | 58 | Linear Feet | Duct Bank Section Q-Q: 2-2" PVC (DIRECT BURIAL) (Refer to Drawing 104 for Duct Bank Details)
7-S | 47 | Linear Feet | Duct Bank Section S-S: 3-4” in Concrete Envelope with rebar (Culvert Crossing) (Refer to Drawing 501 for Duct Bank Details)
7-U | 51 | Linear Feet | Duct Bank Section U-U: 4-6”,4-4" PVC in Concrete/CDF (Refer to Drawing E-104 for Duct Bank Details)
7-V | 20 | Linear Feet | Duct Bank Section V-V: 8-4" PVC in Concrete/CDF (Refer to Drawing E-104 for Duct Bank Details)
7-SL | 3500 | Linear Feet | 1-1" PVC (direct burial) for street lights
8-A | 8 | Each | 6’W x 6’L x 6’-0’D Electric Manhole: Including roadway/sidewalk cutting, excavation, concrete forms (if cast in place), delivery & storage (if precast), concrete, rebar, back fill, heavy duty frame & cover
8-B | 8 | Each | 4’W x 4’L x 4’D Communications Handhole: Including excavation, concrete forms (if cast in place), delivery & storage (if precast), concrete, rebar, back fill, heavy duty frame & cover
8-C | 5 | Each | Furnish & Install Polymer Primary Handhole (24" x 36" x 24")
8-D | 7 | Each | Furnish & Install Polymer Secondary/COMMS. Handhole (24"x24"x24")
9-A | 1 | Each | Switchgear Pad( 4 way gear) 8'-3"L X 6'-0" W X 2'-0" thick
9-B | 1 | Each | Switchgear Pad( 5 way gear) 9'-11"L X 6'-0" W X 2'-0" thick
9-C | 6 | Each | Lateral Feeder Sectionalizing Cabinet Pad (elevated in flood zone)
9-D | 5 | Each | Three Phase Transformer Pad (elevated in flood zone)
9-E | 3 | Each | Single Phase Transformer Pad (elevated in flood zone)
9-F | 1 | Each | Single Phase Transformer Pad (standard)
9-G | 1 | Each | Primary Metering Cabinet Pad (elevated in flood zone)
9-H | 2 | Each | Primary Metering Cabinet Pad (standard)
9-I | 39 | Each | Protective Bollards
10-A | 1 | Lump Sum | Primary riser pole (main feeder) civil work including Rigid Aluminum conduits, concrete encasement, and support brackets, per detail on dwg. #E-100
10-B | 3 | Each | Secondary riser pole civil work including PVC cable sleeve, detail on dwg. E-100
10-C | 1 | Lump Sum | Break into existing manhole #018621 at Nisky Lane and Subase RoaD (Duct Bank D-D and O-O). This work to be performed outside of normal working hours.
10-D | 1 | Lump Sum | Break into existing manhole #010629 at Harwood Highway and Gasvaerks Gade (Duct Bank U-U). This work to be performed outside of normal working hours.
10-E | 9 | Each | Intercept existing primary conduits to refeed existing pad mounted transformer. This work to be performed outside of normal working hours.
10-F | 1 | Lump Sum | Intercept existing primary conduits to refeed existing pad mounted primary load interrupter switchgear on Crown Bay Road. This work to be performed outside of normal working hours.
11-A | 60 | Linear feet | Cut & repair concrete curbs (per detail on Dwg. #G-101)
11-B | 60 | Linear Feet | Cut & repair sidewalks (per detail on Dwg. #G-101)
11-C | 28874.5 | Square Feet | Concrete pavement replacement on public roadway (per detail on Dwg. #G-101)
11-D | 7557.5 | Square Feet | Concrete and Bituminous Pavement Replacement on public roadway (per detail on Dwg. #G-101)
11-E | 3589.875 | Square Feet | Bituminous Pavement Replacement on public roadway (per detail on Dwg. #G-101)
11-F | 1163.95 | Square Feet | Concrete Pavement Patching on private road/drive (per detail on Dwg. #G-101)
12 | 600 | Cubic Yard | Rock Excavation: (allowance)
13 | 1 | Each | Electric manhole evaluation of existing conditions and associated repairs or modifications required (per Dwg. #G-100)
Subtotal Civil
ELECTRICAL WORK
13-A | 3 | Each | Receive, transport, rig & Install pad mounted switchgear (terminations are included under a separate line item)
13-B | 6 | Each | Furnish, transport, rig & install, pad mounted lateral feeder Sectionalizing Cabinet (junctions & terminations are included under separate line items)
13-C | 2 | Each | Receive, transport, rig and install 1 phase, 25kVA transformer (terminations are included under a separate line item)
13-D | 1 | Each | Receive, transport, rig and install 1 phase, 50kVA transformer (terminations are included under a separate line item)
13-E | 1 | Each | Receive, transport, rig and install 1 phase, 75kVA transformer (terminations are included under a separate line item)
13-F | 1 | Each | Receive, transport, rig and install 3 phase, 75kVA transformer (terminations are included under a separate line item)
13-G | 2 | Each | Receive, transport, rig and install 3 phase, 225kVA transformer (terminations are included under a separate line item)
13-H | 1 | Each | Receive, transport, rig and install 3 phase, 300kVA transformer (terminations are included under a separate line item)
13-I | 2 | Each | Receive, transport, rig and install 3 phase, 500kVA transformer (terminations are included under a separate line item)
13-J | 3 | Each | Furnish, transport, rig & install, & connect, primary pad mounted Metering Cabinet, including CT's and PT's and instrumentation wiring
13-K | 3 | Each | Furnish & Install above ground primary pedestal / pull box
14-A | 8 | Each | Furnish & install grounding & bonding in electric manholes per detail on dwg. #E-101
14-B | 3 | Each | Furnish & install grounding & bonding for pad mounted switchgear per detail on dwg. #E-104
14-C | 6 | Each | Furnish & install grounding & bonding for pad mounted sectionalizing cabinet per detail on dwg. #E-104
14-D | 6 | Each | Furnish & install grounding & bonding for 3 phase pad mounted transformer per detail on dwg. #E-105
14-E | 4 | Each | Furnish & install grounding & bonding for 1 phase pad mounted transformer per detail on dwg. #E-104
14-F | 3 | Each | Furnish & install grounding & bonding for primary metering switchgear per detail on dwg. #E-105
14-G | 1 | Each | Furnish & install grounding & bonding for 3 phase Primary Riser Pole per detail on Drawing #E-100
14-H | 3 | Each | Furnish & install grounding & bonding for Secondary Riser Pole per detail on Drawing #E-100
15-A | 47285 | Linear Feet | Receive, pull / install medium voltage main feeder 9A cable (3-1/C #750 kcmil), Tag 1 on dwg. #E-201, termination of cable to be included under cable termination category
15-B | 21796 | Linear Feet | Receive, pull / install 3 phase medium voltage feeder cable (1/C #1/0) tag 2 on dwg. #E-400, termination of cable to be included under cable termination category
15-C | 255 | Linear Feet | Receive, pull / install 1 phase medium voltage feeder cable (1/C #1/0) tag 3 on dwg. #E-400, termination of cable to be included under cable termination category
16-A | 9 | Each | Furnish & Install 15kV Cold Shrink Splices for #1/0 AWG Cable Tag 1A on dwg. #E-400)
16-B | 9 | Each | Furnish & Install 15kV Cold Shrink Splices for #750 kcmil Cable Tag 1B on dwg. #E-400)
16-C | 151 | Each | Furnish & Install 200A, 15kV Elbows (Tag 2A on dwg. #E-400)
16-D | 0 | Each | Furnish & Install 200A, 15kV, fused load break Elbows, with fuses (Tag 3A on dwg. #E-400). Refer to one line diagram for all fuse sizes.
16-E | 214 | Each | Furnish & install Cable Fault Indicators (Tag 4 on dwg. #E-400)
16-F | 76 | Each | Furnish & install Deadbreak Elbows, 600A, 15/25kV (Tag 5 on dwg. #E-400)
16-G | 12 | Each | Furnish & install 15KV Reducing Tap Plug (Tag 6A on dwg. #E-400)
16-H | 34 | Each | Furnish & Install 18kV elbow type Surge Arresters (Tag 7A on dwg. #E-400)
16-I | 13 | Each | Furnish & Install Load Break Feed Thru Inserts (Tag 8A on dwg. #E-400)
16-J | 6 | Each | Furnish & install outdoor termination kits., with support brackets, for #1/0 awg MV Cable (Tag 10A on dwg. #E-400)
16-K | 6 | Each | Furnish & install outdoor termination kits., with support brackets, for #750 kcmil MV Cable (Tag 10B on dwg. #E-400)
16-L | 18 | Each | Furnish & install 4 point, 200A junction (Tag 11B on dwg. #E-400)
16-L | 48 | Each | Furnish & install 4 point, 600A variable junction (Tag 11D on dwg. #E-400)
16-M | 8 | Each | Furnish & install 15kV Insulating Cap for 200A Bushings (Tag 12A on dwg. #E-400)
16-M | 24 | Each | Furnish & install 15kV Insulating Cap for 600A Bushings (Tag 13 on dwg. #E-400)
16-N | 3 | Each | Furnish & install 15kV modular splice kit for #1/0 AWG cable (Tag 14 on dwg. #E-400) complete with T-Body, Insulatng Plugs, Tap Plugs, Connection Plugs, cable adapters and compression lugs
16-O | 1 | Lot | 10% additional MV cable accessories (line item 16A thru 16N) with a minimum of 1 additional accessory.
16-P | 8 | Each MH | Furnish & install manhole accessories for per bill of material on Dwg. E-100
17-A | 1400 | Linear Feet | Furnish & install #600 kcmil cu, 600 volt conductor (secondary)
17-B | 4220 | Linear Feet | Furnish & install #500 kcmil cu, 600 volt conductor (secondary)
17-C | 300 | Linear Feet | Furnish & install #250 kcmil cu, 600 volt conductor (secondary)
17-D | 810 | Linear Feet | Furnish & install #3/0 cu, 600 volt conductor (secondary)
17-E | 450 | Linear Feet | Furnish & install #1/0 cu, 600 volt conductor (secondary)
17-F | 1450 | Linear Feet | Furnish & install #2 cu, 600 volt conductor (secondary)
17-G | 11550 | Linear Feet | Furnish & install #8 cu, 600 volt conductor (from transformers for street lights)
17-H | 18 | Each | Secondary lugs / Terminations (1 phase) at transformer, meter/disconnect
17-I | 48 | Each | Secondary lugs / Terminations (3 phase) at transformer, meter/disconnect
17-J | 1 | Lot | Insulated/weatherproof multi tap connectors in secondary handholes
17-K | 8 | Each | Furnish & install street light fixture, pole, arm, foundation, fuses, and grounding/bonding per street light fixture detail on dwg. #E-100
17-L | 3 | Each | Fiber/Scada for Pad Mounted Switchgear
18-A | 47285 | Linear Feet | Electrical Acceptance Testing for #750 kcmil , 15kV cable
18-B | 22051 | Linear Feet | Electrical Acceptance Testing for #1/0, 15kV cable
18-C | 20180 | Linear Feet | Electrical Acceptance Testing for 600 volt conductors
18-D | 3 | Each | Electrical Acceptance Testing for Pad Mounted Switchgear
18-E | 16 | Each | Electrical Acceptance Testing for pad mounted transformers and primary metering cabinet
19 | 1 | Lot | Electrical Demolition: De-energize, disconnect, remove & dispose of existing electrical equipment as required to clear areas for new construction, in accordance with contract documents (including, but not limited to conduits, pad mounted transformers, MV cable, MV terminations, etc.)
Subtotal Electrical
TOTAL LUMP SUM CONSTRUCTION BID